## Slide 1
LEMUR. University of Oviedo Department of Electrical Engineering – lemur@uniovi.es
Apagón - April 28, 2025

## Slide 2
Overview of April 28
Section 1

## Slide 3: Overview of European grid Frequencies just before the Blackout
Bigger Oscillations
Early Oscillations
DFD
(Market Interval)
Suspicious Events
Normal Events
Iberian Separation
Europe Recovers

## Slide 4: Early Oscillations hint at Instability
From at least 12:13pm* we see notable frequency oscillations in the Iberian grid
Oscillation amplitudes increasing just minutes later
* LEMUR currently only has frequency data from 12:12:51pm – 13:12:50pm
Minor disturbance in Croatia was properly damped and faded in <5 sec. We’ll ignore it.

## Slide 5: Oscillations Worsen Rapidly
Undamped frequencies oscillations rapidly worsen
Note 180° phase shift

## Slide 6: Oscillations Worsen Rapidly
The 15-minute electricity market means many generators change their power setpoints at 12:30pm.
The resulting change in steady-state frequency is called a “Deterministic Frequency Deviation”. These are an undesirable but expected and manageable aspect of large electricity markets.
Iberia still wobbly…

## Slide 7: Iberia Separates from Europe
Significant frequency drop @ 12:32:57.3 is probably not the “15GW in 5 seconds”.
But what is it?
Oscillations persist but Iberia stays connected until…
Fast, irreversible frequency drop starts at 12:32:57.3. Lilely some large source tripped and started the cascade of “15GW in 5 seconds”
Frequency Containment Reserve saturates within 3 seconds.
Rest of Europe actives FCR and stabilizes

## Slide 8
Technical Analysis
Section 2

## Slide 9
LEMUR

## Slide 10
LEMUR is a multidisciplinary research team with researchers belonging to different knowledge areas: Electrical Engineering, Power Electronics and Automation and Control Engineering. The strength is based on looking for synergies and knowledge integration among team members in order to apply for bigger and complex research projects.
OUR GOAL

## Slide 11
To integrate in a laboratory an environment for testing of small scale distributed energy systems and their integration into the electrical grid. For the study and analysis, a four level approach is proposed:
Development of generation systems and power converters for the injection of electrical energy into the grid under efficiency and reliability constraints.
Development of energy storage systems for the compensation of transient demands at the electrical grid, including pulsating generation by renewable energy systems, grid contingencies and virtual zero demanding energy buildings.
Development of coordinated control strategies for all the small scale generators installed at the grid in order the system to behave as a virtual integrated power plant. Development of new power flow algorithms for considering the unbalanced conditions at weak grids (single phase loads and generation systems).
Study of new economic and infrastructure models relying on the distributed generation, which allow to maximize the benefits considering the existing and future regulations.
OUR VISION

## Slide 12
OUR RESEARCH
LINES
ANALYSIS AND DESIGN OF POWER CONVERTER TOPOLOGIES FOR ENERGY STORAGE
  Design of power electronics converters with an emphasis of multiport topologies for energy storage applications
DYNAMIC ANALYSIS AND CONTROL OF POWER CONVERTERS FOR DISTRIBUTED RESOURCES
  High dynamic performance of power converters and microgrids by advanced control systems
POWER FLOW ANALYSIS FOR HYBRID DC/AC GRIDS WITH HIGH PENETRATION OF DISTRIBUTED RESOURCES
  Impact of the integration of distributed resources in the electrical grid
ENERGY DEMAND ANALYSIS AND VISUALIZATION
  Analytic tools and visualization strategies for energy planning
APPLICATIONS
  Industrial applications and knowledge transfer

## Slide 13
THANK YOU!
Any question?