## Slide 1
LEMUR. University of Oviedo Department of Electrical Engineering – lemur@uniovi.es
Apagón - April 28, 2025
Update: May 31, 2025
Authors: Bryan Murray, Dr. Pablo García Fernández

## Slide 2: Disclaimers
The authors* believe there are perfectly plausible technical explanations for the Iberian blackout of April 28, 2025.
The authors are focused on the technical explanations which can be justified with knowledge of the physical infrastructure. In other words, we are not considering cyber-attacks, human errors, or extraordinary meteorological conditions.
For now, we are simply presenting what data we have and will use as a basis for much more engineering analysis.
We are NOT presenting conclusions about root causes.
Why? Because the authors currently lack critical data about the grid’s operational conditions on April 28; for example, details about generators that were online but operating below rated power capacity.
*Report Authors
Lead Author:
  Bryan Murray, P.E. – PhD Candidate
    uo292264@uniovi.es
Reviewer:
  Prof. Pablo García Fernández
    garciafpablo@uniovi.es

## Slide 3
Overview of April 28
Section 1

## Slide 4
Source: El Pais, “¿Qué causó el apagón? Explicación visual y breve de lo que sabemos”

## Slide 5: Overview of European grid Frequencies just before the Blackout
Bigger Oscillations
Early Oscillations
DFD
(Market Interval)
Suspicious Events
Normal Events
Iberian Separation
Europe Recovers

## Slide 6: Early Oscillations hint at Instability
From at least 12:13pm we see notable frequency oscillations in the Iberian grid
Oscillation amplitudes increasing just minutes later
Minor disturbance in Croatia was properly damped and faded in <5 sec. We’ll ignore it.

## Slide 7: Oscillations Worsen Rapidly ~ 12:20pm
Undamped frequencies oscillations rapidly worsen
Note 180° phase shift

## Slide 8: Observing Spurious Oscillations
Oscillations ~0.23 Hz (4.3 seconds)

## Slide 9: Market Change at 12:30pm – No Problem
The 15-minute electricity market means many generators change their power setpoints at 12:30pm.
The resulting change in steady-state frequency is called a “Deterministic Frequency Deviation”. These are an undesirable but expected and manageable aspect of large electricity markets.

## Slide 10: Iberia Separates from Europe
Significant frequency drop @ 12:32:57.3 due to some loss of generation
(link to news conference)
Oscillations persist but Iberia stays connected until…
12:33:16.5: Likely some large source tripped and started the cascade of “15GW in 5 seconds”.**
Rest of Europe actives FCR and stabilizes
Separation from France @ ~12:33:19.4: Rest of Europe recovers, Iberian frequency collapses
** ”desconexión repentina de dos centrales de generación eléctrica en el suroeste de la peninsula” [El Periodico de la Energia, 29 Abril 2025]

## Slide 11: Frequency is consistently to fast all morning
frequency
ascends
within
market
interval!
each

## Slide 12
Rate of Change of Frequency
Section 2

## Slide 13: Rocof Overview
ES_Malaga PMU data did not violate any of the entso-e RoCoF disconnection limits:
> 1.25 Hz/s for 500ms
> 1.5 Hz/s for 1s
> 2 Hz/s for 2s
Instantaneous RoCoF = +0.71 Hz/s

## Slide 14: Rocof stayed within limits
ES_Malaga PMU data* did not violate any of the entso-e RoCoF disconnection limits:
> 1.25 Hz/s for 500ms
> 1.5 Hz/s for 1s
> 2 Hz/s for 2s
Instantaneous RoCoF = -0.8 Hz/s
*Physical RoCoF probably lower, but limited by the PMU recording
RoCoF limits from “Rate of Change of Frequency (RoCoF withstand capability”, entso-e, 31 January 2018

## Slide 15
Generation, Inertia, Exports
Section 3

## Slide 16: Generation MIX on April 28, 2025
Source: ENTSO-E Transparency Platform

## Slide 17: Inertia Estimation Methods – 1 of 2
Grid stability is a complex topic, but two very important factors are controls and inertia.
Controls: Grid-Forming (GFM) controls allow inverter-based resources (“IBR”, e.g. solar, wind, batteries) to positively contribute to grid stability, but these are less prevalent today, and historically most IBRs use grid-following (GFL) controls. New battery installations will greatly expand available GFM assets.
Inertia: ENTSO-E ”Project Inertia” has published basic methods for estimating kinetic inertia, which we utilize in the following slides. These estimates should be considered lower bounds because they do not include:
  Non-generating inertia contributors (e.g. synchronous compensators)
  Inertia from online plants operating below nominal capacity
  Contributions from GFM-capable inverters

## Slide 18: Inertia Estimation Methods – 2 of 2
Inertia estimates are based on standard inertial constants for different generation categories as published in “Inertia and Rate of Change of Frequency (RoCoF)”, ENTSO-E, 16 Dec. 2020
The authors’ lower-bound estimates are based on the simplest data available: generation [MW] by resource type at 12:30pm on April 28, 2025.
Inertia estimates by resource type are simply the product of the that resource’s share of the generation mix [GW/GW] and the inertia constants [s] published by ENTSO-E.
Total equivalent inertia lower-bound estimates is simply the sum of these estimates.
Generation Type | Generation @ 12:30pm (MW) | H_eq (s) | Equivalent Inertia Floor (s) | Generation (%) | Inertia (%)
Solar | 19340 | 0 | 0.00 | 59.8% | 0.0%
Wind Onshore | 3416 | 0 | 0.00 | 10.6% | 0.0%
Nuclear | 3384 | 5.9 | 0.62 | 10.5% | 46.7%
Fossil Gas | 2216 | 4.2 | 0.29 | 6.9% | 21.8%
Hydro Water Reservoir | 1952 | 3.7 | 0.22 | 6.0% | 16.9%
Hydro Run-of-river and poundage | 1184 | 2.7 | 0.10 | 3.7% | 7.5%
Biomass | 356 | 3.3 | 0.04 | 1.1% | 2.7%
Fossil Hard coal | 228 | 4.2 | 0.03 | 0.7% | 2.2%
Waste | 160 | 3.8 | 0.02 | 0.5% | 1.4%
Other renewable | 60 | 3.5 | 0.01 | 0.2% | 0.5%
Hydro Pumped Storage | 36 | 3.5 | 0.00 | 0.1% | 0.3%
Total | 32332 |  | 1.32 | 100.0% | 100.0%
Lower bound estimate!

## Slide 19: Minimum Inertia Estimates for April 28, 2025
Inertia estimate based on actual generation
(lower bound)
Inertia estimates are based on standard inertial constants for different generation categories as published in “Inertia and Rate of Change of Frequency (RoCoF)”, ENTSO-E, 16 Dec. 2020
Connected generators still contribute inertia, even if generating below their rated capacity
Inertia estimation considering connected generation.

## Slide 20
Source: El Pais, “¿Qué causó el apagón? Explicación visual y breve de lo que sabemos”
Iberian connection to France is relatively weak.
France, Germany, and Italy have relatively strong interchange capacity.

## Slide 21
Source: El Pais, “¿Qué causó el apagón? Explicación visual y breve de lo que sabemos”
Iberian connection to France is relatively weak.
France, Germany, and Italy have relatively strong interchange capacity.

## Slide 22: Connections with France
Additional 2.2GW HVDC line expected by 2028
Currently ~2.8GW export capacity
Map Source: ENTSO-E

## Slide 23: Exports to France were below average
~6am, exports to France fall below the seasonal average.
Source: ENTSO-E Transparency Platform

## Slide 24: Conclusions
On April 28th, 2025, the operating conditions on the Spanish grid were challenging, but not unprecedented.
The authors are actively working to reconstruct the grid conditions of April 28 and will continue to publish our findings publicly.
Any feedback or relevant data is appreciated!
  Professor Pablo García Fernández: garciafpablo@uniovi.es
  Bryan Murray: uo292264@uniovi.es

## Slide 25
LEMUR

## Slide 26
LEMUR is a multidisciplinary research team with researchers belonging to different knowledge areas: Electrical Engineering, Power Electronics and Automation and Control Engineering. The strength is based on looking for synergies and knowledge integration among team members in order to apply for bigger and complex research projects.
OUR GOAL

## Slide 27
To integrate in a laboratory an environment for testing of small scale distributed energy systems and their integration into the electrical grid. For the study and analysis, a four level approach is proposed:
Development of generation systems and power converters for the injection of electrical energy into the grid under efficiency and reliability constraints.
Development of energy storage systems for the compensation of transient demands at the electrical grid, including pulsating generation by renewable energy systems, grid contingencies and virtual zero demanding energy buildings.
Development of coordinated control strategies for all the small scale generators installed at the grid in order the system to behave as a virtual integrated power plant. Development of new power flow algorithms for considering the unbalanced conditions at weak grids (single phase loads and generation systems).
Study of new economic and infrastructure models relying on the distributed generation, which allow to maximize the benefits considering the existing and future regulations.
OUR VISION

## Slide 28
OUR RESEARCH
LINES
ANALYSIS AND DESIGN OF POWER CONVERTER TOPOLOGIES FOR ENERGY STORAGE
  Design of power electronics converters with an emphasis of multiport topologies for energy storage applications
DYNAMIC ANALYSIS AND CONTROL OF POWER CONVERTERS FOR DISTRIBUTED RESOURCES
  High dynamic performance of power converters and microgrids by advanced control systems
POWER FLOW ANALYSIS FOR HYBRID DC/AC GRIDS WITH HIGH PENETRATION OF DISTRIBUTED RESOURCES
  Impact of the integration of distributed resources in the electrical grid
ENERGY DEMAND ANALYSIS AND VISUALIZATION
  Analytic tools and visualization strategies for energy planning
APPLICATIONS
  Industrial applications and knowledge transfer

## Slide 29
THANK YOU!
Please get in touch!